Transformer 10000 kVA, UHV=110 kV

Силовий трансформатор ТДТН-10000/110/35/10

Please note that numerical parameters shall be indicated for proposed model(s). Provided parameters must be supported by the relevant document(s), namely (a declaration, certificate, catalogues, data sheets, drawings, manuals, or any other document confirming the fulfillment of the specified)./Будь ласка, зверніть увагу, що числові параметри повинні бути вказані для запропонованих моделей. Надані параметри повинні бути підтверджені відповідним документом(ами), а саме (декларацією, сертифікатом, каталогами, специфікаціями, кресленнями, інструкціями або будь-яким іншим документом, що підтверджує виконання зазначених вимог).

| Item name | Quantity | Delivery point | Vendor addresses of aftersales support in Ukraine |
| --- | --- | --- | --- |
| TDTN type power transformer for voltage class 110/35/10 kV with a capacity of 10 MVA Силовий трансформатор типу ТДТН на клас напруги 110/35/10 кВ потужністю 10 МВА | 1 | DPP Khmelnytskyi, Khmelnytskyi region |  |

| No | TECHNICAL DATA ТЕХНІЧНІ ПАРАМЕТРИ |  |  |  |  |  | Data/значення |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  | Required by the Customer Необхідне Замовнику |  |
| 1. | Technical Data in conformity with the requirements of the standard |  |  |  |  |  | Relevant IEC standards including 60076 valid on the equipment manufacturing date |  |
| 2. | Type designation Тип |  |  |  |  |  | Three-phase, three-winding transformer with OLTC |  |
| 3. | Manufacturer, Model and Country of Origin of the transformer Виробник, модель, країна походження |  |  |  |  |  | To be stated by Manufacturer/ Supplier |  |
| 4. | Installation (Outdoor, indoor) Виконання (зовнішньої, внутрішньої установки) |  |  |  |  |  | Outdoor |  |
| 5. | Type of transformer (single-phase, three-phase) тип трансформатора (однофазний, трифазний) |  |  |  |  |  | three-phase |  |
| 6. | Type of transformer Insulation (oil-filled, dry) Тип ізоляції трансформатора (маслонаповнений, сухий) |  |  |  |  |  | oil-filled |  |
| 7. | Oil expansion compensation (with conservator, hermetic) Компенсація розширення олива (з розширювальним баком, герметичний) |  |  |  |  |  | with conservator |  |
| 8. | Rated capacity, kVA |  |  |  |  | HV ВН | 10000 |  |
|  |  |  |  |  |  | MV СН | 10000 |  |
|  |  |  |  |  |  | LV НН | 10000 |  |
| 9. | Rated frequency, Hz Номінальна частота, Гц |  |  |  |  |  | 50 |  |
| 10. | System nominal voltage, kV Номінальна напруга мережі, кВ |  |  |  |  | HV ВН | 110 |  |
|  |  |  |  |  |  | MV СН | 35 |  |
|  |  |  |  |  |  | LV НН | 10 |  |
| 11. | Highest operating voltage, kV Найбільша робоча напруга, кВ |  |  |  |  | HV ВН | 126 |  |
|  |  |  |  |  |  | MV СН | 40.5 |  |
|  |  |  |  |  |  | LV НН | 12 |  |
| 12. | Short circuit voltage , % Напруга короткого замикання , % |  |  |  |  | HV- MV | 10,5 |  |
|  |  |  |  |  |  | HV- LV | 17,5 |  |
|  |  |  |  |  |  | MV- LV | 6,5 |  |
| 13. | No-load current, % |  |  |  |  |  | 0.7% |  |
|  | Nominal winding voltage (no-load condition), kV Номінальна напруга обмоток (на холостому ході), кВ |  |  |  | HV ВН |  | 115 |  |
|  |  |  |  |  | MV |  | 38.5 |  |
|  |  |  |  |  | LV НН |  | 11 |  |
| 14. | Neutral operating mode (isolated, solid grounded) Режим роботи нейтралі (ізольована, глухозаземлена) |  |  |  | HV ВН |  | solid grounded, can be unearthed |  |
|  |  |  |  |  | MV |  | Isolated |  |
|  |  |  |  |  | LV НН |  | Isolated |  |
| 15. | Maximum short time current (kA) |  |  |  | HV ВН |  | 25 kA (3 s) |  |
|  |  |  |  |  | MV |  | 25 kA (3 s) |  |
|  |  |  |  |  | LV НН |  | 25 kA (3 (s) |  |
| 16. | Winding connection and group Схема з'єднання обмоток і група |  |  |  |  |  | Yn/Yn/D-0-11 |  |
| 17. | Tap changer HV Регулювання напруги ВН |  | Type (OLTC, NLTC) Тип (РПН, ПБВ) |  |  |  | OLTC with vacuum switch |  |
|  |  |  | Range Діапазон |  |  |  | ±9х1,78 % |  |
|  |  |  | Voltage of OLTC drive, V Напруга приводу РПН |  |  |  | AC380/220 V (3ph+N) |  |
| 18. | Tap changer MV Регулювання напруги СН |  | Type (OLTC, NLTC) Тип (РПН, ПБВ) |  |  |  | NLTC |  |
|  |  |  | Range Діапазон |  |  |  | ±2х2,5 |  |
|  |  |  | Voltage of OLTC drive, V Напруга приводу РПН |  |  |  | manual |  |
| 19. | Embedded CT Вбудований трансформатор струму |  | HV ВН |  |  |  | 300-200-150-100/5А, 10P20 20 ВА (2 pcs. in each phase) |  |
|  |  |  | MV СН |  |  |  | not necessary |  |
|  |  |  | HV neutral «0»ВН |  |  |  | 300-200-150-100/5А, 10P20 20 ВА (2 pcs.) |  |
| 20. | OLTC control microprocessor-based device shall be in the scope of supply |  |  |  |  |  | Yes |  |
| 21. | The Cooling system automatics cabinet: |  |  |  |  |  |  |  |
|  | Automatic maintain the temperature inside the cabinet for normal operation in conformity with climatic manufacture version of the transformer equipment; |  |  |  |  |  | Yes |  |
|  | The cabinet protection degree not less than ІР55. |  |  |  |  |  | Yes |  |
|  | Current protection of the fans electric motors. |  |  |  |  |  | Yes |  |
|  | Voltage of fan motors, V (only for ONAF) Напруга двигунів вентиляторів, В (тільки для обдуву) |  |  |  |  |  | AC380/220 V (3ph+N) |  |
|  | The cooling system fans service life, not less than |  |  |  |  |  | 30 years |  |
|  | Coolers Arrangement |  |  |  |  |  | Mounted on the Tank |  |
|  | Cooling Devices (Radiators) Design |  |  |  |  |  | Plated |  |
|  | Automatic Control in Cooling Systems |  |  |  |  |  | Yes |  |
| 22. | Transformer`s coefficient of performance (PEI), % , not less (PEI shall meet the requirements of the ecodesign level 2) |  |  |  |  |  | 99.615% |  |
| 23. | No operating (no-load) Losses at Rated Voltage, (max.) |  |  |  |  |  | According to the regulations on eco-design of power transformers -Supplier to provide value |  |
| 24. | Short-Circuit (load) Losses at rated power in HV-MV mode at middle tap-changer position, (max.) |  |  |  |  |  | According to the regulations on eco-design of power transformers -Supplier to provide value |  |
| 25. | Short-Circuit (load) Losses at rated power in MV-LV mode at middle tap-changer position, (max.) |  |  |  |  |  | According to the regulations on eco-design of power transformers - Supplier to provide value |  |
| 26. | Short-Circuit (load) Losses at rated power in HV-LV mode at middle tap-changer position, (max.) |  |  |  |  |  | According to the regulations on eco-design of power transformers - Supplier to provide value |  |
| 27. | Painting color Колір фарбування |  |  |  |  |  | Light-grey (RAL 7038) |  |
| 28. | Allowable mechanical loads on to the bushings, at least |  |  |  |  |  | IEC 60137 Table 1 |  |
| 29. | Full Wave Lightning Impulse (LI), kV (peak) |  |  | HV ВН |  |  | 550 |  |
|  |  |  |  | MV СН |  |  | 190 |  |
|  |  |  |  | LV НН |  |  | 95 |  |
|  |  |  |  | Neutral HV Нейтраль ВН |  |  | 200 |  |
| 30. | Chopped Wave Lightning Impulse (LIC), kV |  |  | HV ВН |  |  | 605 |  |
|  |  |  |  | MV СН |  |  | 240 |  |
|  |  |  |  | LV НН |  |  | 121 |  |
| 31. | Short-duration (1 min.) powerfrequency withstand voltage (rms), kV (ph-ground/ph-ph) |  |  | HV ВН |  |  | 230 |  |
|  |  |  |  | MV СН |  |  | 85 |  |
|  |  |  |  | LV НН |  |  | 28 |  |
|  |  |  |  | Neutral HV Нейтраль ВН |  |  | 100 |  |
| 32. | Additional devices Додаткові пристрої |  |  | Gas relay for main tank Газове реле |  |  | Yes, Buchholz relay |  |
|  |  |  |  | Temperature indicator Термометр |  |  | Yes |  |
|  |  |  |  | Winding temperature indicator |  |  | Yes |  |
|  |  |  |  | Oil level indicator Вказівник рівня масла |  |  | Yes |  |
|  |  |  |  | Shut-off valve |  |  | Yes |  |
|  |  |  |  | Pressure Relief Valve Запобіжний клапан |  |  | Yes |  |
|  |  |  |  | Silica Gel Фільтр з силікагелем |  |  | Yes |  |
| 33. | Transformer installation (Rollers, Sled, Bottom) Встановлення трансформатора (катки, санки, днище) |  |  |  |  |  | Rollers |  |
| 34. | Transformer connection to the grid with (Bushings, Cable Leads-in, Connection to SF6 conduits) |  |  | HV ВН |  |  | Bushings with RIP internal insulation |  |
|  |  |  |  | MV СН |  |  | Bushings |  |
|  |  |  |  | LV НН |  |  | Bushings |  |
| 35. | External insulation (Porcelain/ polymer/other) |  |  | HV ВН |  |  | Porcelain |  |
|  |  |  |  | MV СН |  |  | Porcelain |  |
|  |  |  |  | LV НН |  |  | Porcelain |  |
| 36. | Range of ambient temperature, °С (min/max) Діапазон температур навколишнього середовища, °С (мін./макс.) |  |  |  |  |  | -45/+45 |  |
| 37. | Specific creepage distance (across the insulator), mm/kV |  |  | HV ВН |  |  | 34.7 (Class C) |  |
|  |  |  |  | MV СН |  |  | 41 (Class C) |  |
|  |  |  |  | LV НН |  |  | 41 (Class C) |  |
| 38. | The maximum thickness of the ice, mm |  |  |  |  |  | 22 mm |  |
| 39. | Climatic Category |  |  |  |  |  | UHL1 |  |
| 40. | Installation altitude m.a.s.l. Висота над рівнем моря, м. |  |  |  |  |  | <1000 m |  |
| 41. | Seismic stability, not less, MSK-64 points Сейсмостійкість за шкалою MSK-64, балів |  |  |  |  |  | 7 |  |
| 42. | The permissible noise level at the distance 2 m, dB |  |  |  |  |  | <85 |  |
| 43. | Service life, years, not less than Строк експлуатації, років, не менше |  |  |  |  |  | 30 |  |
| 44. | Warranty period, years, not less than Гарантія, років, не менше |  |  |  |  |  | 5 |  |
| 45. | «Impact-indicators» on the transformer for movement conditions monitoring within the shipping time period. 3-Axis recordings. |  |  |  |  |  | Yes |  |
| 46. | Possibility of monitoring system installation and transformer connection to Power Automation and Control Systems (PACS) in future |  |  |  |  |  | Yes |  |
| 47. | Movement on site should be possible on rails |  |  |  |  |  | Yes |  |
| 48. | Rollers with ribs |  |  |  |  |  | Yes |  |
| 49. | Width of rail, mm | For longitudinal movement |  |  |  |  | 1524 |  |
|  |  | For transverse movement |  |  |  |  | 2000 |  |
| 50. | Stainless steel hose along the transformer tank to protect the control cables laid from the monitoring, signaling, protection devices, leads-in, the current transformers to the terminals cabinets, against mechanical damage and solar radiation |  |  |  |  |  | Yes |  |
| 51. | Scope of supply |  |  |  |  |  |  |  |
|  | The cooling system automatics cabinet in complete set |  |  |  |  |  |  |  |
|  | The control cables complete set with protection for the cables to be laid along the tank |  |  |  |  |  |  |  |
|  | Spares in conformity with the Supply Complete Set Data Sheet, set |  |  |  |  |  |  |  |
|  | Additional amount of oil for process operations and replenishing during installation works |  |  |  |  |  |  |  |
| 52. | Documents to be supplied |  |  |  |  |  |  |  |
|  | Complete Set Data Sheet |  |  |  |  |  |  |  |
|  | Quality Certificate |  |  |  |  |  |  |  |
|  | Certificates for transformer and completing parts (products) of the system |  |  |  |  |  |  |  |
|  | Technical Description and Operation Manuals or Operation Guidelines (which include the planned repair documentation) for the transformer, completing parts and systems |  |  |  |  |  |  |  |
|  | Origin Certificate |  |  |  |  |  |  |  |
|  | Control diagrams of the Cooling Systems and OLTC |  |  |  |  |  |  |  |
|  | Acceptance Tests report (Certificates) |  |  |  |  |  |  |  |
| 53. | Delivery (with/without oil) - (in case of transportation with no oil, the complete set includes the transformer oil in the amount, required for filling-in, process operations during the erection and oil additional filling-in up to the operation oil level). |  |  |  |  |  | With |  |
| 54. | - The Supplier shall provide a qualified representative(s) on site for installation and commissioning supervision if it is necessary to ensure the manufacturer's warranty. The appropriate representative(s) shall perform supervision on all tasks during unloading, unpacking, erection and commissioning of the transformer. Taking into account the current situation regarding security risks in Ukraine remote (using photo and video surveillance) supervision could also be acceptable. Постачальник повинен надати кваліфікованого(их) представника(ів) на будмайданчику для нагляду за монтажем та введенням в експлуатацію (шеф монтаж), якщо це необхідно для забезпечення гарантії виробника. Відповідні представники повинні здійснювати нагляд за всіма діями під час розвантаження, розпакування, монтажу та введення трансформатора в експлуатацію. Беручи до уваги поточну ситуацію щодо ризиків безпеки в Україні, дистанційний (з використанням фото- та відеоспостереження) нагляд також може бути прийнятним. |  |  |  |  |  | Yes / Так |  |